## Summary
Code | Section | Total £
A | Strip-out + enabling
B | Mechanical first-fix
C | HEPA AHU install (CDP)
D | Electrical install (CDP)
E | BMS integration
F | Builders work + finishes
G | Commissioning + handover
P | Preliminaries
R | Risk allowance
OH | OH&P
TOTAL | TENDERED SUM (excl. VAT)

## §A
A · Strip-out + enabling
Item | Description | Unit | Qty | Rate £ | Amount £
A.01 | HCAI dust segregation hoarding Floor-to-ceiling polyethene hoarding with airlock entry · 24 lm | lm | 24 | 460
A.02 | Temporary AHU + filtered duct discharge Hire + install + commissioning + removal · 18 weeks | item | 1 | 32680
A.03 | Strip-out FCUs + existing ductwork 6 × FCUs · ductwork · grilles · diffusers · controlled disposal | nr | 6 | 1600
A.04 | Electrical containment + cable strip-out Existing 1st-fix containment, cabling, accessories | m² | 280 | 26
A.05 | Ceiling tile + grid strip-out Suspended ceiling system to slab · ~280 m² gross | m² | 280 | 18
A.06 | Partition + floor finish strip-out Existing internal partitions + vinyl floor finishes | m² | 280 | 22
A.07 | Controlled waste removal + disposal Segregated waste · BREEAM diversion · 92% target | item | 1 | 12200
Subtotal · A · Strip-out + enabling

## §B
B · Mechanical first-fix
Item | Description | Unit | Qty | Rate £ | Amount £
B.01 | CHW primary header rework + tie-in Existing chiller plant retained · header rework · tie-in to new distribution | item | 1 | 28500
B.02 | Distribution pipework + insulation CHW + LPHW distribution · BS 5422 insulation | lm | 120 | 145
B.03 | FCU install + commissioning 6 × 2-pipe FCUs · Trust framework · supply + install | nr | 6 | 4200
B.04 | Medical gas first-fix containment + brackets O2 / Vac / MA / AGSS per bay · BS 5682 compliant | nr | 4 | 5400
B.05 | Pressure-test + flush Full system pressure-test + chemical flush · witnessed | item | 1 | 8500
B.06 | Mechanical sundries + fixings Brackets · supports · valves · gauges · sundries | item | 1 | 6700
B.07 | Mech first-fix labour element Mechanical foreman + ops · site supervision · QA | item | 1 | 13100
Subtotal · B · Mechanical first-fix

## §C
C · HEPA AHU install (CDP)
Item | Description | Unit | Qty | Rate £ | Amount £
C.01 | HEPA AHU · Howorth Air Tech 5 m³/s · H14 filter bank · 14-wk lead · supply only · framework supplier | nr | 1 | 178400
C.02 | Crane lift + position Lifting plan · crane hire · structural sign-off (T03 hold point) | item | 1 | 14200
C.03 | Ductwork connections + transitions Supply + extract ductwork tie-in to AHU · insulated · acoustic | lm | 65 | 360
C.04 | Pressure-differential controls + validation tappings Magnehelic gauges · validation tap points · DPS sensors | nr | 6 | 1800
C.05 | Thermal + acoustic insulation AHU casing + ductwork · acoustic dampening · pressure jacketing | item | 1 | 16700
C.06 | CDP design + calc submission Class 3 cleanroom CDP submission · calcs · validation methodology | item | 1 | 14200
C.07 | Mech install labour element Specialist install + co-ordination · 4 wks @ 2 ops + foreman | item | 1 | 22700
Subtotal · C · HEPA AHU install (CDP)

## §D
D · Electrical install (CDP)
Item | Description | Unit | Qty | Rate £ | Amount £
D.01 | TP&N sub-main · 250A MICC sub-main from existing 200A spare · sized to 250A (AS-06) | lm | 38 | 285
D.02 | Distribution boards · 2 × DB Type-tested boards · 18-way · MCB schedule · labels | nr | 2 | 4400
D.03 | LED clinical-grade luminaires IP44 recessed · CRI ≥80 · 4000K · 300/1000 lx clinical | nr | 38 | 380
D.04 | IPS-backed emergency lighting at treatment bays BS EN 60601-1 · emergency drivers · 3-hr sustain BS 5266 | nr | 12 | 720
D.05 | Nurse call extension · Static SOLO C5 Extension to existing Trust system · 6 call stations + 4 receivers | item | 1 | 14400
D.06 | Power final circuits + dado containment Twin + dedicated outlets · dado containment · MICC drop | nr | 38 | 240
D.07 | CDP design + IPS sub submission IPS + lighting CDP submission · BS 7671 18th Ed compliance | item | 1 | 8800
D.08 | Electrical install labour element Specialist install + supervision · NICEIC accredited | item | 1 | 89970
Subtotal · D · Electrical install (CDP)

## §E
E · BMS integration
Item | Description | Unit | Qty | Rate £ | Amount £
E.01 | Trent BMS panel + I/O modules Trent expansion · BACnet IP · 120 hard + 24 soft I/O | nr | 1 | 14200
E.02 | BMS field wiring I/O wiring · terminations · sensor inputs · valve outputs | lm | 180 | 38
E.03 | Front-end licence extension Existing Trent front-end licence extended (QT-09 confirmed) | item | 1 | 3800
E.04 | BMS graphics + point schedule Custom graphics for chemo prep + treatment bays · alarms | item | 1 | 4200
E.05 | BMS commissioning + witness 144 I/O points exercised · Trust BMS Lead witnessed | item | 1 | 8960
Subtotal · E · BMS integration

## §F
F · Builders work + finishes
Item | Description | Unit | Qty | Rate £ | Amount £
F.01 | Slab core penetrations · HCAI wet-cut + LEV Up to 300mm slab cores · LEV extraction · HCAI-compliant | nr | 14 | 850
F.02 | Fire-stopping at penetrations All slab + wall penetrations · 2-hr FR · CE-marked products | nr | 24 | 280
F.03 | Suspended ceiling install · HEPA-compatible Grid + tile · HEPA-compatible · 280 m² gross | m² | 280 | 64
F.04 | Vinyl floor finishes Polysafe Hydro Evolve or VE alternative · welded seams · coving | m² | 280 | 78
F.05 | Decoration · low-VOC paints Trust standard scheme · low-VOC EN 14785 · 2-coat finish | m² | 760 | 14
F.06 | Partition reinstate + adjustments Minor partition works · door re-hangs · architrave · MF ceiling soffits | item | 1 | 18980
Subtotal · F · Builders work + finishes

## §G
G · Commissioning + handover
Item | Description | Unit | Qty | Rate £ | Amount £
G.01 | 14-day commissioning burn-in AHU at design conditions · particle baseline · DPS log | item | 1 | 14200
G.02 | Class 3 particle count + smoke test ISO 14644-1 Class 3 · smoke visualisation · Trust IPC witness | item | 1 | 8400
G.03 | HEPA integrity test (0.3 μm) BS EN ISO 14644-3 · all HEPA filters · accredited tester | item | 1 | 6800
G.04 | Mechanical balance + flow proportional HTM 03-01 Part B · BSRIA standard · ITP-04 witnessed | item | 1 | 7600
G.05 | NICEIC inspection + test + certs BS 7671 18th Ed · earth loop · insulation · NICEIC pack | item | 1 | 4800
G.06 | IPS battery duration test (3-hr) BS EN 60601-1 · drop test · Trust EE + AP-ME witness | item | 1 | 3200
G.07 | O&M manuals + as-builts + handover pack Digital + hardcopy · BIM-compatible · as-installed records | item | 1 | 9800
G.08 | Training delivery + DLP setup 2 training sessions · 12-month DLP undertaking · spares list | item | 1 | 9200
Subtotal · G · Commissioning + handover

## §P
P · Preliminaries
Item | Description | Unit | Qty | Rate £ | Amount £
P.01 | Welfare compound · 18 weeks Toilets · drying · mess · lockers · located off-site at Mitie compound | wk | 18 | 850
P.02 | Site management · Project Manager + Site Manager Jack Connor PM · Mike Whitlock SM · 18 weeks | wk | 18 | 3800
P.03 | Commissioning Lead · Sarah Patel AP-ME · 8 weeks active commissioning · 2 wks pre-comm planning | wk | 10 | 2800
P.04 | HCAI dust monitoring + IPC liaison Daily HCAI inspections · monitoring · Trust IPC liaison | wk | 18 | 480
P.05 | Plant hire · 18 weeks Tower scaff · MEWP · podium · sundries | wk | 18 | 480
P.06 | PI 12-year run-off premium Broker confirmed cover (QT-14) · 12-yr run-off · £4,200 absorbed | item | 1 | 4200
P.07 | Performance bond · 10% On-demand bond · PC + 12mo · banking fees | item | 1 | 11200
P.08 | DBS + Trust induction · 8 ops DBS clearance + Trust HCAI induction · 8 operatives | nr | 8 | 220
P.09 | Documentation + reporting Weekly + monthly reports · RAMS pack · ITP register · QA pack | wk | 18 | 220
P.10 | Other prelims sundries Stationery · IT · phones · vehicle running · sundries | item | 1 | 1900
Subtotal · P · Preliminaries

## §R
R · Risk allowance
Item | Description | Unit | Qty | Rate £ | Amount £
R.01 | Operational risk allowance 5% of measured-works · operational delivery risk · per PR-01 to PR-08 | item | 1 | 42000
Subtotal · R · Risk allowance

## §OH
OH · OH&P
Item | Description | Unit | Qty | Rate £ | Amount £
OH.01 | Overheads & Profit Includes head-office overheads, contract margin and tendered profit | item | 1 | 171000
Subtotal · OH · OH&P